## Instructions, Version History
Instructions
RC users will need to upload their incremental updates for the Network Model through the RIMS Reliability Coordinator UI. At a minimum, each submission must include the following: - Network Model Scope Template file - Supplemental files, as needed. Please refer to the Non CIM Equipment Model Checklist tab of this checklist or the CIM Model Checklist.
Non CIM Equipment Model Checklist tab | This tab identifies which files are required for specific Equipment Type Modeling updates. This is a general checklist used by the ISO for TO/BA Data Requests listing the data that is required to connect equipment to the network model.
CIM Model Checklist | This tab identifies which files are required for CIM Modeling updates.
Supporting Documentation Definition tab | This tab provides definitions to the requested supplemental files for modeling submissions.
WEIM Gen tab | This tab identifies which additional files and requirements are needed for an RC-WEIM generator change.
Additional Resources | Modeling Changes User Guide for RC West Customers: https://rc.caiso.com/Documents/Modeling-Changes-User-Guide.pdf RC0120 Document: http://www.caiso.com/Documents/RC0120.pdf RC0120A Document: http://www.caiso.com/Documents/RC0120A.xlsx
Version History
Version Number | Changes | Effective Date
1 | Document created. | 2019-12-19
2 | Equipment Based Checklist Implemented; Supporting Documentation Definition Tab Created. Addition of CIM Model Checklist Tab. | 2020-07-08
2.1 | Updated descriptions of CIM file, Single Line Diagrams, and ICCP. Denoted that ICCP file should be provided in full. Added RAS ICCP Template. Updated that ratings are provided via the RC Data Gathering Template for Non CIM. | 2020-11-02
2.2 | Updated to include JOU-Dynamic Template information and requirements | 2021-04-01
2.3 | WEIM Gen Tab - Addition of SC Relinquish Document Type | 2021-04-23
2.4 | WEIM Gen Tab - Minor clarifications; Align submission process for Row 12-16; Added requirement for resource requesting ISO Forecast. Supporting Doc Definition Tab - Addition of forecasting requirements including Site Info, Topo Map & Metrological Data | 409892
2.5 | Addition of the "Extreme Weather" Template & the "List of BES Exceptions" in the Supporting Doc Definition tab, Non CIM Equip. Model Checklist & CIM Model Checklist. | 2022-11-01
2.6 | Addition of the "System Voltage Limits" Template in the Supporting Doc Definition tab. | 2023-02-13
2.7 | Addition of the "FERC881 Dynamic MVA ICCP" Template and "Shunt Equipment Data" Template in the Supporting Doc Definition tab. | 2023-10-06

## Non CIM Equip. Model Checklist
Non CIM Equipment Model Checklist
Equipment Type (Drop Down List in Network Scope Document) | Data requested in Supporting Documentation | Documents required to submit via RIMS UI
Transmission Lines | 1. One-line diagrams of both substations at each end of the transmission line, Series Capacitor, or Series Reactor 2. Impedance (R and X)-PU 3. B-PU 4. Area and Zone 5. Ratings (Summer Normal, Summer Emergency, Winter Normal, Winter Emergency) 6. ICCP if available 7. Dynamic Limits if applicable 8. Line Routing 9. English Name Mapping | 1: Single Line Diagram 2-4: Model File 6: ICCP SCADA Mapping Template 5, 7-9: RC Data Gathering Template 8: Shapefile
Shunt Cap\Reactor\SVD's | 1. B-PU 2. Area and Zone 3. B actual 4. Voltage Deadband PU 5. B-step and #of Steps 6. ICCP if Available 7. Automatic regulation set points (Voltage Set Points ) (if applicable) 8. Normal On/Off setting | 1-5: Model File 6: ICCP SCADA Mapping Template 7-8: RC Data Gathering Template
Transformers | 1. If the transformer is a 2-winding transformer: 1. Impedance 2. MVA Base 3. Type (Fixed, Auto LTC, Manual LTC) 4. Regulating Bus (if any) 5. Side on which the LTC is located (high/low) 6. From nominal voltage 7. To nominal voltage 8. From Fixed Tap 9. To Fixed Tap 10. Max variable tap 11. Min variable tap 12. Max constant V 13. Min constant V 14. Step size 15. Ratings (Summer Normal, Summer Emergency, Winter Normal, Winter Emergency) 16. Area and Zone 2. If the transformer is a 3-winding transformer: (include the parameters requested for 2-winding transformers above plus) 1. Tertiary and internal bus parameters 2. Impedance from primary to tertiary 3. Tertiary nominal voltage 4. Tertiary Fixed Tap 3. If the transformer is a phase shifter: (include the parameters requested for 2-winding transformers above plus) 1. Variable Angle 4. ICCP if Available 5. English Name Mapping | 1-3: Model File 4: ICCP SCADA Mapping Template 5: RC Data Gathering Template
Substation\Load | 1. Bus # 2. Bus Name 3. Nominal Voltage 4. Scheduled Voltage 5. Max Voltage 6. Min Voltage 7. Area and Zone 8. Change files (i.e. Breaker configuration, Voltage level upgrade, Equipment moving from one bus to another, Etc.) Are there Load Banks added 1. PLOAD 2. QLOAD 3. Area and Zone 9. ICCP if Available 10. Substation Coordinates | 1-7: Model File 8: Model File or RC Data Gathering Template 9: ICCP SCADA Mapping Template 10: RC Data Gathering Template
RAS | 1. Specify if the RAS is a new or existing RAS 2. Provide all RAS points with their SCADA/ICCP IDs (RAS points status) should be sent to CAISO with the same convention as the CB/DSC status points as follow: • RAS ENABLED and RAS ARMED needs to be sent with the same convention for CB being CLOSED • RAS DISABLED and RAS DISARMED needs to be sent with the same convention for CB being OPEN 3. Provide a screenshot of the display built showing the RAS/SPC points if Available (Screenshot in .pdf or .jpg format) | 1-2: RAS ICCP Mapping Template 3: RAS Display Screenshot
Breaker(s)\Disconnect(s) | 1. One-line diagram showing the location of the shoofly 2. One-line diagrams of both substations at each end of the shoofly 3. In-Service Date 4. Impedance (R and X)-PU 5. B-PU 6. Ratings (Summer Normal, Summer Emergency, Winter Normal, Winter Emergency) 7. Area and Zone | 1: Single Line Diagram 2 & 4 : RC Data Gathering Template 3: ICCP SCADA Mapping Template
Shoofly Install\Removal | 1. One-line diagram showing the location of the shoofly 2. One-line diagrams of both substations at each end of the shoofly 3. In-Service Yes/No 4. Impedance (R and X)-PU 5. B-PU 6. Ratings (Summer Normal, Summer Emergency, Winter Normal, Winter Emergency) 7. Area and Zone | 1-2: Single Line Diagram 3-7: Model File or RC Data Gathering Template
Synchronous Condenser | 1. Qmax/Qmin Limits 2. Scheduled Voltage 3. Base MVA 4. Single Line Diagram showing the location of the Condenser 5. ICCP if Available 6. Dynamic data file in PSLF format with mapping to the RDFID in the power flow/CIM format 7. English Name Mapping | 1-3: Model File 4. SLD 5: ICCP SCADA Mapping Template - Full list if possible 6: dyd Mapping template 7. RC Data Gathering Template
Contingency Definition | 1. For each Line, Transformer, Substation configuration modification, submit the new updated contingency definition that would represent the protection clearing zone (i.e. identify the Circuit Breakers that would be opened to clear fault in that particular line or transformer) | 1: Contingency Definition Template
Generator | 1. Pmax 2. D-Curve Reactive power limit 3. Scheduled Voltage 4. Base MVA 5. Single Line Diagram showing the location of the unit 6. ICCP 7. Dynamic data file in PSLF format with mapping to the RDFID in the power flow/CIM format 8. English Name Mapping 9. JOU and Dynamic Schedules information and/or estimated D_Curves for JOUs 10. Cold weather attributes | 1-4: SGIT & Model File 5: SLD 6: ICCP SCADA Mapping Template - Full list if possible 7: Dynamic Model & dyd Mapping template 8: RC Data Gathering Template 9. JOU-Dynamic Template 10. Extreme Weather Template
Note on C7: Arechavaleta, Marissa: Remove SPS & RL to confirm if we need display thru rims

## CIM Model Checklist
CIM Model Checklist
CIM Model Submission | Data requested in Supporting Documentation | Documents required to submit via RIMS UI
CIM Model | 1. CIM File 2. ICCP 3. Ratings (If not included in the CIM file) 4. Dynamic Ratings 5. Station Coordinates 6. Line Routing 7. English Name Mapping (If different than the names in the CIM File) 8. GRDT or SGIT update for new resources 9. Contingency Template 10. Dynamic Data 11. RAS Screenshot 12. JOU and Dynamic Schedules information and/or estimated D_Curves for JOUs 13. Cold weather attributes for new resources | 1: Model File 2: ICCP SCADA Template - Full List 3-7: RC Data Gathering Template 6: Shapefile 8: GRDT or SGIT 9: Contingency Definition Template 10: Dynamic Model & dyd Mapping template 11: RAS ICCP Mapping Template & RAS Display Screenshot 12. JOU-Dynamic Template 13. Extreme Weather

## Supporting Doc Definition
Model Update Document Submission Definitions
Supporting Documentation | Template Location | RC0120A Request Number | Document Filename Title All files uploaded to RIMS should be clearly labeled. Include the filename convention within the filename of the document/file as an indicator of the deliverable. Each file name must include the DocumentTitle and Version#. | Additional Information
Network Model Scope Template *Required for any model change | RIMS Downloads | N/A | Scope Template | Entity: Short Name Equipment Type: Choose from the drop down List of associated documents uploaded: List filenames of supporting documentation uploaded to the RC File upload section that supports this change Substation Name: Location of change Effective Date of Change: Date this change is be effective Requested Model Build for change to be included in: Model build number intended to be included in Short Description: High level description of the change
CIM XML (Version 15 or 10), PSSE, PSLF, PowerWorld or Model Report File (Excel) | N/A | 6.1 | Model File | The full CIM XML export of the model that includes the new network topology changes for generation, transmission, and load equipment and facilities may be submitted using CIM15 or CIM10 formats.
Single Line Drawings | N/A | 6.1 | SLD | Single line drawings are required to be construction grade. RC West prefers single line diagrams (SLD) of each change to the transmission project in line of the move program so each change is easily identifiable. SLDs shall be provided from CIM submitting entities upon RC West request.
ICCP SCADA Mapping | RIMS Downloads | 6.1 | ICCP | The Inter-Control Center Protocol (ICCP) document for mapping transmission assets is essential to running the power transmission grid. RC users should provide a line item on the Network Model Scope Template indicating the ICCP changes. The full ICCP list that maps to the CIM XML model should be provided. RAS ICCP points can be provided on separate tab of ICCP SCADA Mapping Template.
Supplemental Generator Information Template (RC Only Customers) Generation Resource Data Template (RC-WEIM Customers) | SGIT: RIMS Downloads GRDT : http://www.caiso.com/market/Pages/NetworkandResourceModeling/Default.aspx | 6.8.1 | SGIT or GRDT | RC West customers should include information for each of their generators on an SGIT. If the resource is already in the model, then this document can be processed in 10 business days. If the resource is not in the model or an existing resource is requesting a Pmax increase greater than its nameplate rating , then it will be included with the model update timeline. If you are an RC-WEIM customer, please submit the Generation Resource Data Template found in the Resource data submission section of the Network and Resource Modeling page on caiso.com.
RC Data Gathering Template | RIMS Downloads | 6.10, 6.13, 6.14, 6.15, 6.17, 6.23 | RC Data Gathering Template | RC users can use the RC Data Gathering Template to submit several IRO-010 requirements, as needed, in one document: • 6.10: Facility ratings and overload relay trip settings (including time-delay) on those Facilities (transformers and transmission lines) that are part of Bulk Electric System and their overload trip settings are below 125% of the highest Facility rating • 6.13: State, city, longitude and latitude for each substation with voltage levels > 100kV or with total plant generation >= 50MW • 6.14: Line routing for all lines 100kV and above • 6.15: List of shunt devices normally on AVR. These shunts are those that can automatically connect/disconnect at a specified voltage setpoint without operator intervention. The list shall include the voltage setpoint(s) and any time delays prior to automatic switching. • 6.17: List of all normally open circuit breakers, disconnects and switches that control the connectivity of transmission branch elements and Facilities; list shall include unique status for all applicable seasons. • 6.23: Equipment Long Name to RDFID mapping - There should have only one row per RDFID and there should be no empty rows. For the Long Name, customers can choose any name with no special characters and it is not longer than 30 characters.
Shapefile | N/A | 6.13, 6.14 | Shapefile | In addition to the 6.13 and 6.14 sections of the RC Data Gathering Template, RC Users must submit shapefile for transmission lines, but it is optional for generation. For GIS data, shapefiles are required for transmission lines as this contains all the required coordinates forming the line and it will not have the CIM_FROM_SUB and CIM_TO_SUB fields available by default. If the CIM_FROM_SUB and CIM_TO_SUB columns can be added to the shapefile, the template is not needed.
Contingency Definition Template | https://mpp.caiso.com/sites/RIMS/_layouts/download.aspx?SourceUrl=/sites/RIMS/BulkLoadTemplates/RC/Contingency Definition Template.xlsx | 6.24 | Contingency Definition | Contingency definitions are used by our operations engineers to define contingencies used in the network model applications. Please only submit additions, updates, and deletions to the existing contingencies.
RAS Display Screenshot | N/A | 6.26 | RAS Display | Provide a screenshot of the display built showing the RAS/SPC points if Available (Screenshot in .pdf or .jpg format)
dyd Mapping template | RIMS Downloads | 6.25 | dyd Mapping | Dynamic data file in PSLF format with mapping to the RDFID in the powerflow/CIM format
Dynamic Model for Transient Stability Analysis | N/A | 6.25 | Dynamic Model | This data can be provided in the same GE PSLF format that is being submitted to WECC base case development. It is important to provide clear mapping between the EMS model to the GE PSLF dynamic model. Synchronous machine RDFIDs are provided on the RC Portal > Western Interconnection Model library > Generating Resources in RC West area.
RAS ICCP Mapping | RIMS Downloads | 6.18 | RAS ICCP | The Inter-Control Center Protocol (ICCP) document for mapping transmission assets is essential to running the power transmission grid. RC users should provide a line item on the Network Model Scope Template indicating the RAS ICCP changes.
JOU and Dynamic Template | RIMS Downloads | 6.16 | JOU-Dynamic | This document is used to provide information for Pseudo Ties, Jointly Owned Units and Dynamic Schedules
Site Information Sheet | Solar and Wind Site Information Sheet (Found under Bucket 1 of the NRI website) ) | Tariff Appendix Q | SiteInfo | Site Information Form must be completely filled out before uploaded to RIMS. For plant location, the Eligible Intermittent Resource must use latitude and Longitude expressed in degrees/decimals using WGS84 geodetic datum only. Supplemental information may be required if the information provided on the information sheet is insufficient to generate a forecast. NOTE: If the Resource will be sharing meteorological data with another resource, then contracts between the host plant and the shared plant will be required. http://www.caiso.com/CBT/Forecasting/Forecasting.html
Topographical Map |  | Tariff Appendix Q | TopoMap | The topographical map is submitted for renewable resources only. This is a topographical plot plan map that depicts all the boundaries of the site and the topology of the land for forecasting purposes. The map must identify all meteorological stations and turbine/panel location by latitude and longitude and should be in degrees/decimals using WGS84 geodetic datum only. See the Tariff Appendix Q for more information about this requirement. For wind resources the purpose of this document is for our engineers to utilize the locations of turbines and the topology of the land to determine the designated turbines that will be used for forecasting purposes. A wind resource will need to illustrate the location and height for each wind turbine within a wind park. http://www.caiso.com/CBT/Forecasting/Forecasting.html
Meteorological Data | RIMS Downloads | Tariff Appendix Q | ICCP | The meteorological data is submitted for renewable resources receiving an ISO forecast. Please refer to the Tariff Appendix Q for meteorological requirement specifics. http://www.caiso.com/CBT/Forecasting/Forecasting.html
Extreme Weather | RIMS Downloads | 6.8.2 | Extreme Weather | The Extreme Weather template is available for entities to submit their generator's cold weather attributes. RC Data Request 6.8.2
List of BES Exceptions | RIMS Downloads | 4.10 | Exception | The list of BES exceptions template is available for entities to submit the list of BES exceptions, which should include the list of facilities that are “Not in the normal bright line 100kV” in accordance with NERC’s BES definition and guidelines. The list should include all facilities < 100 kV that are considered BES as well as the list of all facilities > 100 kV that are considered NOT BES.
System Voltage Limits | RC Portal | 4.9 | System Voltage Limit | TOPs shall review their System Voltage Limits annually at a minimum and document changes to their System Voltage Limits. TOPs must use the template posted to RC West’s portal titled “System Voltage Limits TEMPLATE.xlsx” to communicate their System Voltage Limits. TOPs shall post the populated template for its TOP Area in the “SOL Methodology” library in the secure RC West portal and also upload to the RIMS application (per the RC model update process). TOPs shall submit the completed spreadsheet with the filename “System Voltage Limits – TOPxyz.xlsx”. When a TOP posts an update to the “System Voltage Limits” folder, the TOP must delete prior versions and fill out the “Revision History” tab in the updated System Voltage Limits. Note that prior versions deleted from the folder are available for viewing in the Archive library.
Shunt Equipment Data Template | RC Portal | 6.15 | Shunt Equipment | List of shunt devices normally on AVR. These shunts are those that can automatically connect/disconnect at a specified voltage setpoint without operator intervention. The list shall include the voltage setpoint(s) and any time delays prior to automatic switching.
FERC881 Dynamic MVA ICCP Template | RIMS Downloads | 6.10.2 | Dynamic MVA ICCP | Dynamic Facility Ratings on those Facilities (transformers and transmission lines) that are part of Bulk Electric System. Entities can fill out up to 4 emergency ratings in MVA, that are in ascending order. It is recommended that entities determine the minimum and maximum reasonability limits for each equipment based on seasonal limits (+/- 15% of seasonal limit).

## WEIM Gen
Model Update Submission Type: CIM
Document Name | Template Location | ISO Reference Document | Document Filename Title All files uploaded to RIMS should be clearly labeled. Include the filename convention within the filename of the document/file as an indicator of the deliverable. Each file name must include the DocumentTitle and Version#. | Additional Information | Days before implementation date | Submission Process | Adding a Resource | Changing Resource: Non-Participating to Participating | Changing Resource: Participating to Non-Participating | Changing Resource: Market Parameters (Pmax Increase) | Changing Resource: Market Parameters (anything other than Pmax) | Removing a Resource | Changing Resource: Requesting ISO Forecast (Existing Resource)
Network Model Scope Template *Required for any model change | https://mpp.caiso.com/sites/RIMS/_layouts/download.aspx?SourceUrl=/sites/RIMS/BulkLoadTemplates/RC/Network Model Scope Template.xlsx | https://www.westerneim.com/Pages/Resources.aspx | Scope Template | Entity: Short Name Short Description: High level description of the change List of associated documents uploaded: List filenames of supporting documentation uploaded to the RC File upload section that supports this change Substation Name: Location of change Effective Date of Change: Date this change is be effective Requested Model Build for change to be included in: Model build number intended to be included in | FNM schedule customer submission deadline applicable for the target implementation date | Upload to RIMS | Required | N/A unless existing resource requesting ISO forecast | N/A unless existing resource requesting ISO forecast | Required | N/A | Required - Submit after resource is permanently retired and not coming back | Required
CIM XML (Version 15 or 10) | N/A | N/A | Model File | Incremental network topology changes for generation, transmission, and load equipment and facilities may be submitted using one or more of the Network Model Data Formats. When submitting CIM file updates, ensure this CIM file has the following new/updated resource information for future changes: Substation/voltage information at interconnection point Anticipated Pmax Resource ID Prior to the customer submission deadline please provide the complete CIM file which includes the new/updated resource. | FNM schedule customer submission deadline applicable for the target implementation date | Upload to RIMS | Required | N/A unless existing resource requesting ISO forecast | N/A unless existing resource requesting ISO forecast | Required | N/A | Required | Required
JOU and Dynamic Transfers |  | N/A | JOU -Dynamic | List of Pseudo Ties and Jointly Owned Units if the Owner BA. List of Dynamic Schedules if the Owner BA as requested by the RC. | FNM schedule customer submission deadline applicable for the target implementation date | Upload to RIMS | Required | Required | Required | Required | N/A | Required | N/A
Site Information Sheet Document Title: SiteInfo | Solar and Wind Site Information Sheet (Found under Bucket 1 of the NRI website) ) | Tariff Appendix Q | SiteInfo | Site Information Form must be completely filled out before uploaded to RIMS. For plant location, the Eligible Intermittent Resource must use latitude and Longitude expressed in degrees/decimals using WGS84 geodetic datum only. Supplemental information may be required if the information provided on the information sheet is insufficient to generate a forecast. NOTE: If the Resource will be sharing meteorological data with another resource, then contracts between the host plant and the shared plant will be required. | FNM schedule customer submission deadline applicable for the target implementation date | Upload to RIMS | Required if requesting ISO forecast | N/A unless existing resource requesting ISO forecast | N/A unless existing resource requesting ISO forecast | N/A unless existing resource is currently ISO forecasted | N/A | N/A | Required
Topographical Map Document Title: TopoMap (See Guideline Above) |  | Tariff Appendix Q | TopoMap | The topographical map is submitted for renewable resources only. This is a topographical plot plan map that depicts all the boundaries of the site and the topology of the land for forecasting purposes. The map must identify all meteorological stations and turbine/panel location by latitude and longitude and should be in degrees/decimals using WGS84 geodetic datum only. See the Tariff Appendix Q for more information about this requirement. For wind resources the purpose of this document is for our engineers to utilize the locations of turbines and the topology of the land to determine the designated turbines that will be used for forecasting purposes. A wind resource will need to illustrate the location and height for each wind turbine within a wind park. | FNM schedule customer submission deadline applicable for the target implementation date | Upload to RIMS | Required if requesting ISO forecast | N/A unless existing resource requesting ISO forecast | N/A unless existing resource requesting ISO forecast | N/A unless existing resource is currently ISO forecasted | N/A | N/A | Required
Meteorological Data |  | Tariff Appendix Q & ICCP SCADA Mapping | ICCP | The meteorological data is submitted for renewable resources receiving an ISO forecast. Please refer to the Tariff Appendix Q for meteorological requirement specifics. | FNM schedule customer submission deadline applicable for the target implementation date | Upload to RIMS | Required if requesting ISO forecast | N/A unless existing resource requesting ISO forecast | N/A unless existing resource requesting ISO forecast | N/A unless existing resource is currently ISO forecasted | N/A | N/A | Required
Project Details Form (Create SCME Project Type) | Project Details Form | http://www.caiso.com/participate/Pages/NewResourceImplementation/Default.aspx | ProjectDetailsForm | Submitting this online form will assign the project an internal CAISO Project code. All documentation must reference this code in the required file naming convention. Project Details Forms are needed to gather specific details about your project and to determine in which Full Network Model (FNM) build your project can be included. Note: If your proposed project requires more than one market resource ID you will need to create one project per resource ID. For example, if the project is a large solar resource requiring two market resource IDs, two Project Details Forms will be required. | Email submission to NRI@caiso.com ----------------- Submit no later than 40 calendar days | Submit to NRI@caiso.com ---------------- Follow NRI Checklist for filename submission (include NRI project code) | Required | Required | Required | N/A | N/A | N/A | N/A
ISO Meter Configuration Worksheet (SCME) | BPM for Metering | Meter Configuration Worksheet --------------------------- SQMD plan template; SQMD plan template for additional metering devices. | SQMD MeterConfig | The purpose of the SQMD plan template is to verify the physical metering standards and resource algorithms. Please note that the Site Owner is responsible for the accuracy of the information on this form. | 35 calendar days prior | Submit to NRI@caiso.com ---------------- Follow NRI Checklist for filename submission (include NRI project code) | Required | Required | Required | N/A | N/A | N/A | N/A
Single Line - IFC Electrical Drawings | BPM for Direct Telemetry | Single Line Drawing Requirements can be found under Metering Documentation Guidelines | SLD | Issued For Construction (IFC) Drawings should comply with Section 18 of BPM for Direct Telemetry and BPM for Metering for CAISO review. | 35 calendar days prior | Submit to NRI@caiso.com ---------------- Follow NRI Checklist for filename submission (include NRI project code) | Required | Required | Required | N/A | N/A | N/A | N/A
SCME PE Stamp Attestation Letter | N/A | N/A | Attestation | If a Scheduling Coordinator Metered Entity does not have a Local Regulatory Authority, or if their Local Regulatory Authority does not have any Metering standards set, then Scheduling Coordinator Metered Entities are required to meet California ISO Metering standards. CAISO requires Single Line drawings that are either “Issued for construction” or “As- Built”. All the “Issued for Construction” drawings are required to be stamped by a Professional Engineer (PE). In the absence of the Professional Engineer stamp, CAISO accepts an attestation letter. Stamp Attestation letter must be from the Electrical Engineer and it should state that the Single Line Drawing is the exact physical and electrical representation of the resource. | 35 calendar days prior | Submit to NRI@caiso.com ---------------- Follow NRI Checklist for filename submission (include NRI project code) | If Applicable | Required | Required | N/A | N/A | N/A | N/A
Generation Resource Data Template | https://www.westerneim.com/Pages/Resources.aspx | https://www.westerneim.com/Documents/EIM-Procedure-For-Non-Participating-And-Participating-Resources.pdf | GRDT | If you are an RC-WEIM customer, please submit the Generation Resource Data Template found in the Integrate with the ISO full network model section on the westerneim.com website. | 30 Calendar Days | Submit to CIDI | Required | Required | Required | Required - Update via the Master File UI once the change has been implemented in the model | Required - Update via the Master File UI at least 5 days prior to implementation | N/A | N/A
New Scheduling Coordinator Selection Letter | http://www.caiso.com/participate/Pages/SchedulingCoordinatorOngoingObligations.aspx | https://www.westerneim.com/Documents/EIM-Procedure-For-Non-Participating-And-Participating-Resources.pdf | SCSelection | Effective date of assignment must match that in the SC Acceptance letter. The association process takes 5-11 business days to complete. | 30 Calendar Days | Submit to CIDI | Required | Required | Required | N/A | N/A | N/A -------- Notify SC Requests | N/A
New Scheduling Coordinator Acceptance Letter | http://www.caiso.com/participate/Pages/SchedulingCoordinatorOngoingObligations.aspx | https://www.westerneim.com/Documents/EIM-Procedure-For-Non-Participating-And-Participating-Resources.pdf | SCAcceptance | Effective date of assignment must match that in the SC Selection letter. The association process takes 5-11 business days to complete | 30 Calendar Days | Submit to CIDI | Required | Required | Required | N/A | N/A | N/A | N/A
Relinquishing SC letter | N/A | https://www.westerneim.com/Documents/EIM-Procedure-For-Non-Participating-And-Participating-Resources.pdf | SCRelinquish | When a WEIM resource is shutting down and is being removed from the model, a Relinquishing SC letter is required for EIM participating and non-participating resources. If the resource is an EIM Participating Resource, then the Resource Owner letter is also required and the schedule 1 needs to be updated to remove the resource. | 30 Calendar Days | Submit to CIDI | N/A | N/A | N/A | N/A | N/A | Required | N/A
Resource Control Agreement Form | http://www.caiso.com/Documents/ISOAffiliationResourceControlAgreementDisclosureForm.xls | N/A | N/A | Used for Market Monitoring for Market Power Analysis. This must be submitted at the same time as the GRDT. In addition provide the project code and SQMD/SDL acceptance date of the NRI project. | 30 Calendar Days | Submit to CIDI | Required | Required | Required | N/A | N/A | N/A | N/A